## Table 1
CODE No. [DN] | Item | Description | At shipment | NOTES
1 | Filter display delay timer | 0000 : None 0001 : 150H 0002 : 2500H 0003 : 5000H 0004 : 10000H | 0002 : 2500H
2 | Dirty state of filter | 0000 : Standard 0001 : High degree of dirt (Half of standard time) | 0000 : Standard
3 | Central control address | 0001 : No.1 unit to 0064 : No.64 unit 0099 : Unfixed | 0099 : Unfixed
4 | Specific indoor unit priority | 0000 : No priority 0001 : Priority | 0000 : No priority
6 | Heating temp shift | 0000: No Shift 0001: +1.8° F(2°C) 0002: +3.6°F(2°C) to 0010: +18°F(10°C) (Up to +6° recommended) | 0002: +3.6°F (2°C) (Floor type 0000: 0°C)
OC | Preparing Indication Selection | 0000: Preparing indicated 0001: No Indication | 0000: Preparing indicated
0D | Existence of AUTO Mode | 0000: Provided 0001: Not Provided (Automatic selection from connected outdoor unit) | 0001: Not Provided
0E | FS Box | 0000: Only 1 indoor unit on FS 0001: More than 1 indoor unit | 0000: Standard
0F | Cooling only | 0000 : Heat pump 0001 : Cooling only (No display of [AUTO] [HEAT]) | 0000 : Heat pump
10 | Type | 0001: 4-Way Air Discharge Cassette 0004: Standard Ducted 0005: Slim Duct 0006: High Static Ducted 0007: Under Ceiling 0008: High Wall 0014: Compact 4 Way | Depending on model type
11 | Indoor unit capacity | 0000 : Unfixed 0001 to 0041 See Page 50 SHRM Quick Reference | According to capacity type | 0000:Invalid 0001: 007 0003: 009 0005: 012 0007: 015 0009: 018 0010: 021 0011: 024 0012: 027 0013: 030 0015: 036 0016: 042 0017: 048 0018: 056 0021: 072 0023: 096
12 | Line address | 0001 : No.1 unit to 0030 : No.30 unit | 0099 : Unfixed
13 | Indoor unit address | 0001 : No.1 unit to 0064 : No.64 unit | 0099 : Unfixed
14 | Group address | 0000 : Individual 0001 : Header unit of group 0002 : Follower unit of group | 0099 : Unfixed
16 | Fan Speed Selection | 0001:A 0002: L 0003: A+L 0004: M 0006:A+L+M 0008: High 0010:A+L+H 0012:M+H 0015: All Speeds | 0015: All Speeds Except HSD=0008
18 | Timed Operation | Timer 10 Minutes Heat 5 minutes Cool 0000- Off 0001- Active | 0000- Off
19 | Louver type (Air direction adjustment) | 0000: No Louver 0001: Swing only 0002: (1-Way ADC, UC) 0003: (2-Way ADC) 0004: (4-Way ADC) | According to type | ADC = Air Discharge Cassette UC = Under Ceiling
1E | Temp difference of [AUTO] mode selection COOL → HEAT, HEAT → COOL | 0000 : 0° to 0010 : 10° (For setup temperature, reversal of COOL/HEAT by ± (Data value)/2) | 0003 : 3 deg (Ts±1.5)
22 | Min setting temp Heating (remote) | Setting range in Celsius Only -15 to 60 (5.0F to 140.0F) | 18 Celsius (64.4F)
25 | Max setting temp Auto (remote) | Setting range in Celsius Only -15 to 60 (5.0F to 140.0F) | 29 Celsius (84.2F)
26 | Min setting temp Auto (remote) | Setting range in Celsius Only -15 to 60 (5.0F to 140.0F) | 18 Celsius (64.4F)
28 | Automatic restart of power failure | 0000 : None 0001 : Restart | 0000 : None
2A | Selection of option/error input (CN70) | 0000 : Filter input 0001 : Alarm input (Air washer, etc.) 002 : None | 0002 : None
2b | Thermo Output | 0000: Indoor thermostat on 0001: ON receiving output of outdoor compressor | 0000: Thermo on
2E | HA terminal (CN61) select | 0000 : Usual 0001 : Leaving-ON prevention control 0002 : Fire alarm input | 0000 : Usual (HA terminal)
31 | Ventilating fan control | 0000 : Unavailable 0001 : Available | 0000 : Unavailable
32 | TA sensor selection | 0000 : RTA sensor 0001 : Remote controller sensor | 0000 : RTA sensor
33 | Temperature unit select | 0000 : °C (at factory shipment) 0001 : °F | 0001 : °F
36 | Room Temp Display | 0000: Display Setpoint 0001: Display Room Temp | 0000: Setpoint
40 | Humidifier Control | Drain pump control 0003: Humidifier on Drain Off | 0003: Humidifier on Drain Off
42 | Self Clean Operation Time (4 way Cassette Only) | 0000: None 0000: .5h to .012: 0h | 0002: 1 hour | Set when compressor-ON time is 10 to 60 minutes When ON time is 60 minutes or more, the double of this operation time setting is set.
45 | Selection of louver horizontal discharge position (4-Way Air Discharge Type Only) | 0000: Smudging less setting 0002: Cold draft preventing setting | 0000: Smudging-less setting
C2 | Current Demand X% to outdoor unit | 0050: 50% 0100: 100% | 0075: 75%
CC | Setting of self-clean operation forced stop (4-Way cassette type only) | 0000: No 0001: Yes | 0000: None | Clean operation is performed in case of stop by HA input Clean operation is not performed in case of stop bt HA input HA operation output OFF during clean operation in case of stop by remote controller HA operation output ON during clean operation in case of stop by remote controller
CD | Clean operation stop function when [ON/OFF] operation is prohibited. (4-Way cassette type only) | 0000: Valid (clean operation) 0001: Invalid (no clean operation) | 0000: Valid | The air conditioner stops (including fire arlarm such as remote monitor system) while setup of [ON/OFF] operation prohibited (Central 1,2) is performed from central controller side.
CE | Domestic/Overseas | 0000: Domestic 0001: Overseas | 0000:
C5 | Flip of AUX Heat | 0000 Standard 0001 Flip
C6 | Outdoor Temp Enable AUX Heat | 0001 to 00031=5 to 59
C7 | Additional setting of outdoor range | 0001 to 0010=.9 to 18F
DB | Diff T Secondary Heat | Setting Cut in - Cut out differential of secondary heat 0001 to 0010 0000: 0*F 0001:=1*F 0010:=9*F 0005&6=5*F
DC | Delta T Secondary Heat | Setting enables secondary heat and disables cooling signal CN60 0000: None 0001: to 0010 0001:=1*F 0010:=9*F 0005&6=5*F | 0000: None
dO | Remote save operation | Remote controller operation save function | 0001: Enable
D1 | Frost prevention/Objective Heating | 0000: Impossible 0001: Valid | 0000: None
D3 | Revolution frequency of self clean operation ( 4-Way cassette Type Only) | 0000: Invalid 0001: Valid | 0001: Valid ( 210 rpm / operation)
D4 | Display / No display of [Dry Operation] during self clean operation (4-Way Air Discharge Type Only) | 0000: Display 0001: No Display | 0000: Display
EO | For North America | 0000: 0001: North America
5D | High Ceiling Static Adjustment | Slim,high static ducted 0000:Lo 0001:Medium 0003:Hi Hi 0006:Lo Lo 4-Way, High Wall 0000: Lo 0001:Medium 0003: Hi | 0001:Standard (slim, high static ducted) 0000:Standard (4-Way cassette, medium static) 0000: Standard (Ceiling)
60 | Timer Set (Wired Remote) | 0000: Available 0001: Unavailable | 0000: Available
60 | Timer setup (Wired remote controller) | 0000: Available (Operable) 0001 : Unavailable (Operation prohibited) | 0000 : Available
69 | Louver Position Selection Cooling | 0000: Normal 0001: Down Allowed | 0000: Normal
7A | Change unit +0.9°F(0.5°C) or +1.8°F(1.0°C) on remote | 0000 : +0.9°F(0.5°C) 0001 : 1.8°F(1.0°C) | 0000 : +0.9°F(0.5°C)
E0 | Region | 0000: Japan Model 0001 : North America model | 0001 : North America model
72 | Fan Control in Defrost | 0001-Forced fan stop in Defrost 0000-Normal Fan operation | 0000:
77 | Setpoint | 0000: Single setpoint auto 0002: Dual setpoint auto
86 | Correction of feeling of strong heating | 0000: Not provided 0001: Provided | 0000: Not Provided
92 | Outside interlock release condition | 0000: Operation Stop 0001:Release communication signal receive | 0000: Operation Stop
9A | Fan Control Cooling | 0000: Standard 0001:L to LL | 0000: Default
9B | Hot Start Fan Heating | 0000- Normal fan starts by TC Sensor 0001- No fan stop Defrost LL 0002-No hot start control-speed set by remote controller | 0000: Default
F0 | Swing Mode | 0001: Standard 0002: Dual 0003: Cycle 0000: No Synchronization | 0001: Standard
F1 | Fixed Louver position (Louver No.1) | 0000: Release 0001: Horizontal position 0005: Downward discharge position | 0000: Not Fixed
F2 | Fixed Louver position (Louver No.2) | 0000: Release 0001: Horizontal position 0005: Downward discharge position | 0000: Not Fixed
F3 | Fixed Louver position (Louver No. 3) | 0000: Release 0001: Horizontal position 0005: Downward discharge position | 0000: Not Fixed
F4 | Fixed Louver position (Louver No. 4) | 0000: Release 0001: Horizontal position 0005: Downward discharge position | 0000: Not Fixed
FE | 1 FS Box and multiple Indoor Wired Remotes | 0000: Only 1 remote per group 0001: Individual Remote
7A | Temperature Increment | 0000: 2 Degree F 0001: 1 Degree F | 0000: 2 Degree F
1F | Max setting temp Cooling (remote) | Setting range in Celsius Only -15 to 60 (5.0F to 140.0F) | 29 Celsius (84.2F)
20 | Min setting temp Cooling (remote) | Setting range in Celsius Only -15 to 60 (5.0F to 140.0F) | 18 Celsius (64.4F)
21 | Max setting temp Heating | Setting range in Celsius Only -15 to 60 (5.0F to 140.0F) | 29 Celsius (84.2F)
103 | Remote controller | 0000: Use 0001 : Do not use (Indoor unit production after Jun-2021 does not need this DN setting. The serial number is 12600001 or upper.) | 0000: Use